- 手动平板闸阀概述：

● 制造与验收技术条件按日本火力发电用阀门标准E101和JB/T3595-93的规定；

● 结构长度按E101的规定或按用户提供尺寸

● 焊接坡口接电力工业管理标准78DG的规定或按用户提供尺寸。

● The manufalture and aueptanle specigication shan be based on the japanese standard E101 applied for the thermal powerand JB/T3595-93

● The length shall bein line with E101 or by user’s speeification.

● Welding groove shan be in auordanle with power industrh spe-cification 78DG or hg user’ specification

● The size in inclose is old production’s size

- 性能规范Property and specifiecation

| 产品型号 Product type公称压力PN(MPa)Nominal pressure |  | 试验压力(MPa)Test pressure |  | 工作压力(MPa)Working pressure | 工作温度(℃)Working temperature | 适用介质Appicable medium |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 强度试验Sheel test | 密封试验/上密封实验Seal test |  |  |  |
| Z960Y-250 | 25 | 37.5 | 27.5 | - | ≤425 | 水、蒸汽、Water,steam |
| Z960Y-320 | 32 | 48.0 | 36.0 | - | ≤425 |  |
| Z960Y-P54100 | - | 30.0 | 22.0 | P5410 | ≤540 | 蒸汽 Steam |
| Z960Y-P54170 | - | 48.0 | 36.0 | P5417 | ≤540 |  |
| 主要零件材料Matecrial for main parts |  |  |  |  |  |  |
| 零件名称Part name |  | 材料牌号Material designation |  |  |  |  |
| 阀体Body |  | WCB |  | WC6 |  | WC9 |
| 阀板Disc |  | WCB |  | WC6 |  | WC9 |
| 阀盖Bonnet |  | 25 |  | 12Cr1Mo1VA |  |  |
| 阀杆Stem |  | 1Cr17Ni2 |  | 20Cr1Mo1VA |  |  |
| 阀座Seat |  | 25 |  | 12Cr1Mo1VA |  |  |
| 密封环Sealing ring |  | S软钢(增强柔性石墨)S soft steel (flexible graphite) |  | S软钢S soft steel |  | F软钢F Soft steel |
| 填料Packing |  | 增强柔性石墨Fexible graphite |  |  |  |  |
| 支架Yoke |  | WCB |  | WCB或WC6 |  |  |
| 阀杆螺母Stem nut |  | 45(ZCuZn25A16Fe3Mn3) |  |  |  |  |
| 四开环Four piece ring |  | 1Cr13 |  | 20Cr1MoVA |  |  |

- 主要尺寸及重量Main dimensions and weight

| 公称通径DNNominal diameter | 主要外形尺寸和连接尺寸(mm)Main external and connecting dimensions |  |  |  |  | 电动装置Electric dewice | 重量(kg)Weight |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | d | L | H | L1 | L2 |  |  |
| Z60Y-250 |  |  |  |  |  |  |  |
| 100 | 84 | 406 | 1164 | 437 | 277 | DZW45 | 234 |
| 125 | 100 | 483 | 1402 | 437 | 277 | DZW60 | 343 |
| 175 | 158 | 711 | 1650 | 554 | 309 | DZW180 | 638 |
| 225 | 200 | 864 | 1650 | 554 | 309 | DZW180 | 654 |
| 300 | 280 | 1067 | 2106 | 764 | 398 | DZW350 | 1973 |
| Z60Y-320 |  |  |  |  |  |  |  |
| 100 | 96 | 533 | 1236 | 437 | 277 | DZW60 | 291 |
| 125 | 118 | 610 | 1302 | 437 | 277 | DZW60 | 315 |
| 150 | 148 | 762 | 1403 | 526 | 283 | DZW90 | 672 |
| 175 | 148 | 762 | 1650 | 554 | 309 | DZW180 | 684 |
| 225 | 222 | 1041 | 1650 | 554 | 309 | DZW180 | 696 |
| Z60Y-P54100V |  |  |  |  |  |  |  |
| 175 | 148 | 762 | 1650 | 554 | 309 | DZW180 | 683 |
| 225 | 222 | 1041 | 1650 | 554 | 309 | DZW180 | 704 |
| 250 | 222 | 1041 | 1795 | 554 | 309 | DZW180 | 1214 |
| 300 | 294 | 1245 | 2080 | 554 | 309 | DZW250 | 2125 |
| Z60Y-P54170V |  |  |  |  |  |  |  |
| 125 | 98 | 630 | 1230 | 437 | 277 | DZW60 | 312 |
| 225 | 186 | 1060 | 1680 | 554 | 309 | DZW180 | 1401 |
| 300 | 278 | 1397 | 2265 | 764 |  | DZW500 | 2834 |
| 325 | 310 | 1448 | 2265 | 690 | 398 | DZW500 | 2632 |
| 350 | 338 | 1550 | 2536 | 715 |  | DZWC-4 | 5591 |